Clinic fit-out  |  Room data sheets

Room Data Sheet: Outpatient Exam Room
Typical exam room, 10.8 m2. Applies to rooms EX-01 to EX-12.
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Typical layout (dimensions in mm).
General
	Item
	Requirement

	Function
	Patient consultation and physical examination

	Area
	10.8 m2 (3600 x 3000)

	Ceiling height
	2700 mm

	Occupancy
	1 patient, 1 clinician, 1 companion


Finishes
	Surface
	Finish

	Floor
	Sheet vinyl, welded seams, coved 100 mm up the wall

	Walls
	Washable paint, impact-resistant to 1200 mm

	Ceiling
	600 x 600 hygiene tiles, clip-in

	Door
	1000 mm leaf, vision panel, privacy curtain inside


Building services
	Service
	Requirement

	General lighting
	500 lux at couch, Ra 90 or higher, 4000 K

	Examination light
	Wall-mounted arm, 20,000 lux at 0.5 m

	Power
	4 double sockets (2 at desk, 2 at couch)

	Data
	2 outlets at desk, 1 for wall monitor

	Ventilation
	6 air changes per hour, supply and extract

	Water
	Hands-free basin with lever tap, 40 deg C max

	Nurse call
	Pull cord at couch, indicator over door


Furniture and equipment
	Item
	Qty
	Supply

	Examination couch, height adjustable
	1
	Owner

	Desk with lockable drawer
	1
	Contractor

	Clinician chair
	1
	Owner

	Visitor chair
	2
	Owner

	Wall-mounted sharps and glove holders
	1
	Contractor

	Wall monitor arm
	1
	Contractor


Room data sheets describe the briefed requirement. Drawings govern dimensions.

