# Lighting Design Report: Level 3 Office Fit-Out

Design stage report, revision B. Calculations for maintained illuminance, uniformity and lighting power density.

# 1. Summary

This report sets out the lighting design for the Level 3 office fit-out (about 1,150 m2). All spaces meet the target maintained illuminance and uniformity with LED luminaires. The installed lighting power density is 5.6 W/m2 against a code allowance of 8.9 W/m2, a 37% margin.

Open office: 532 lux average on the work plane, uniformity 0.64.

Meeting rooms: 388 to 455 lux with separate presentation scene.

All luminaires dimmable (DALI) with daylight sensors in the perimeter zone.

Emergency lighting to 1 lux on escape routes, 3 hour duration.

# 2. Design criteria

| Space | Target (lux) | Uniformity min. | UGR max. | Ra min. |
| --- | --- | --- | --- | --- |
| Open office | 500 | 0.6 | 19 | 80 |
| Meeting rooms | 400 | 0.6 | 19 | 80 |
| Reception | 300 | 0.4 | 22 | 80 |
| Corridors | 150 | 0.4 | 25 | 80 |
| Break room | 200 | 0.4 | 22 | 80 |
| Print room | 300 | 0.4 | 22 | 80 |

# 3. Calculation method

Calculations use a 0.25 m grid on a 0.75 m work plane, with reflectances of 70% (ceiling), 50% (walls) and 20% (floor). A maintenance factor of 0.80 is applied, based on a clean office, 3 year cleaning cycle and L80 lumen maintenance at 50,000 hours.

Figure 1. Open office isolux plot: six 600 x 1200 luminaires per bay.

# 4. Results

Figure 2. Target and calculated average illuminance by space.

| Space | Area (m2) | Luminaires | Avg (lux) | Min/avg | W/m2 |
| --- | --- | --- | --- | --- | --- |
| Open office | 640 | 96 | 532 | 0.64 | 5.9 |
| Meeting 1 | 42 | 6 | 455 | 0.71 | 6.1 |
| Meeting 2 | 36 | 4 | 388 | 0.66 | 4.8 |
| Reception | 85 | 10 | 341 | 0.52 | 4.4 |
| Corridor | 180 | 22 | 172 | 0.47 | 3.1 |
| Break room | 95 | 9 | 236 | 0.58 | 3.9 |
| Print room | 22 | 2 | 298 | 0.61 | 3.6 |

# 5. Controls

Each open-office bay is a DALI group with an occupancy sensor (15 minute hold) and a daylight sensor for the first 4.5 m from the facade. Meeting rooms have a four-button scene panel: Full, Presentation (front row at 20%), Video call (vertical illuminance on faces 250 lux) and Off.

# 6. Luminaire schedule

| Type | Description | Lumens | Watts | CCT | Qty |
| --- | --- | --- | --- | --- | --- |
| L1 | Recessed panel 600 x 1200, opal | 4400 | 34 | 4000 K | 96 |
| L2 | Recessed panel 600 x 600, opal | 3200 | 26 | 4000 K | 20 |
| L3 | Downlight 150 dia., wide beam | 1800 | 15 | 3000 K | 34 |
| L4 | Linear pendant, up/down | 5200 | 42 | 3500 K | 9 |
| EM1 | Emergency bulkhead, 3 h | 300 | 3 | 5000 K | 18 |

# 7. Open items

Confirm ceiling void depth above meeting rooms (duct clash, see RFI 014).

Client to approve 3500 K for the break room pendants.

Commissioning plan to be issued with the controls submittal.