Community library extension  |  RFI log

Request for Information 014
Luminaire clash with supply duct, corridor 2.
	Field
	Entry

	RFI no.
	014

	Date raised
	Week 17

	Raised by
	Main contractor, site manager

	To
	Services engineer

	Drawings
	E-201 Rev C (lighting), M-201 Rev D (ductwork)

	Response needed by
	Week 19


Question
In corridor 2 between grid lines 4 and 6, the 600 x 300 supply duct runs directly above the line of recessed luminaires type L2. The luminaire housing is 140 mm deep but there is only about 20 mm clear between the top of the ceiling grid and the underside of the duct. Please advise how to resolve.
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Sketch: section through corridor 2 at grid 5.
Options considered by the contractor
1. Lower the corridor ceiling from 2700 to 2550 mm (affects door heads, needs architect approval).
2. Replace L2 with a surface-mounted slim luminaire (30 mm deep).
3. Offset the luminaires 400 mm to one side of the duct (affects uniformity).
4. Re-route the duct as two 600 x 150 ducts (needs fan duty check).
Response
(To be completed by the services engineer.)
	Field
	Entry

	Answer
	

	Cost impact
	Yes / No

	Programme impact
	Yes / No

	Responded by
	

	Date
	


Response requested within 5 working days to avoid programme delay.

