## Slide 1
Warehouse High-Bay LED Upgrade
Business case
Replacing 180 metal halide high-bays

## Slide 2
Today
2
• 180 x 400 W metal halide high-bays, 12 m mounting height
• Lights run 24 hours, 6 days a week
• Average 140 lux at floor level; target is 200 lux for picking aisles
• Re-strike delay of 10 minutes after power dips
• Annual lighting energy about 410,000 kWh

## Slide 3
Option comparison
3
 | Keep metal halide | LED high-bay | LED + aisle sensors
Fixtures | 180 | 150 | 150
Watts each | 455 | 150 | 150
Average lux | 140 | 220 | 220
Energy (MWh/yr) | 410 | 113 | 62
Capital cost ($) | 0 | 96,000 | 118,000
Annual saving ($) | - | 38,600 | 45,200
Payback (years) | - | 2.5 | 2.6

## Slide 4
Annual energy by option (MWh)
4
Chart: 
| Keep metal halide | LED high-bay | LED + aisle sensors
MWh per year | 410 | 113 | 62

## Slide 5
Cumulative savings ($ thousands)
5
Chart: 
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
LED high-bay | -96 | -57.4 | -18.8 | 19.8 | 58.4 | 97 | 135.6 | 174.2 | 212.8
LED + aisle sensors | -118 | -72.8 | -27.6 | 17.6 | 62.8 | 108 | 153.2 | 198.4 | 243.6

## Slide 6
Recommendation
6
• Choose LED high-bays with aisle occupancy sensors
• Install over four weekends, one zone at a time
• Apply for the utility rebate before ordering (about $21,000)
• Measure light levels before and after for the record